## Sheet1
NAME OF WORK: QUICK WATERING SYSTEM AT PLATFORM NO. 7,8,9 &10 OF PRAYAGRAJ RAILWAY STATION.
BOQ
Sl. No. | Item Description | Qty | UOM | Rate | Amount
1 | Submission of GA, Power & control circuit diagram, complete working principle, arctitectural drawing, wiring diagram, logic, IO's list, termination schedule, Operation & Maintenance Manual as per technical document for approval. | 1 | Job |  | 0
2 | Cloud based SCADA (Licensed). Internet connection with minimum 20 Mbps downlink speed will be provided by railways. At the time of commissioning temporary internet facility shall be provided by MTPL. | 1 | Job |  | 0
3 | Control Panel (inclusion of the following (i) to (ix)) - (i) Design, fabrication, transportation, supply, erection and commissioning of LT cubical panel 3 Phase and neutral 415V. 4 Wire, free standing floor mounted, LT panel made up of 14SWG CRCA (Cold Rolled Carbon Annealed) sheet after seven tank process and painting with EPOXY powder coating. The panel shall consist of suitable rating TPN (Triple pole neutral) tinned copper bus bar supported with DMC/AMC barriers and colour coded with heat shrinkable sleeves. The metering shall be provided as specified The panel shall have short circuit with standing capacity of minimum SOKA (RMS) power frequency test and consist of the switch gear as mentioned below. The panel shall be mounted on channels including supply and fixing as per specification. The complete work has to be carried out by the vendor . All the feeder cables have to be connected to the panels with suitable cable glands as per the requirement at site. Air condition provision is to be made for entire control panel. The panel consists:- (ii) 1 No. of 400A, 4 Pole, 36KA,MCCB (Moulded case circuit breaker) & 400 AP changeover for incoming (iii) 5 No. of 125A, 10KA 4 Pole MCCB out going. (iv)1 No. of 36A, 10KA 4 Pole MCB (Miniature circuit breaker) out going (v) 5 No. of 32 A,10KA 4 Pole MCB out going (vi) Along with multifunctional digital meter similar to model No: EM-VIFPE of M/s HPL make with suitable ratios CTs(Current transformer) along with the selector switches, LED phase indication pilot lamps (3No's), and tinned copper bus bar of 1000V along with rubber chequered sheets of size 1m length of panel of 12 mm thick as per IS 5424-1 No. complete (vii) Suitable set of capacitor as per pump capacity required with auto manual APF Relay. (viii) VFD (Variable frequency Drive) 60HP 1 No. PLC 1 No. HMI, with pressure treasures. (ix) Suitable 60 HP star delta starter with auto manual selection mode and same starter will work on VFD and command will be to VFD by PLC (Programmed Logic Control). Complete with PLC CPU and requiered AI, AO, DI, DO cards. | 1 | Set |  | 0
4 | Smart Control to operate QWS through mobile. | 1 | Numbers |  | 0
5 | Connection of all type of Power & Control cables for interconnection between control panel to UPS, PC & other system and field items such as Pumps, Pressure Transmitter, Flow Meter, Electrical Valve along with all necessary accessories like glands, terminal, lugs etc. | 1 | Job |  | 0
6 | Earthing erection with GI strip and its connection | 4 | Numbers |  | 0
7 | Report Generation as per Approved format. | 1 | Numbers |  | 0
Total Quoted Value |  |  |  |  | 0
Total Value (Including GST) |  |  |  |  | 0